I. Temperature stability in the MMF:                                               Achim Weidemann Oct.4, 2006

The figures above,

2006-9-20_0-0-0_to_2006-10-4-_20-49-26-Undulator17Temps.jpg

2006-9-20_0-0-0_to_2006-10-4-_20-49-26-Undulator102Temps.jpg

show the total time history of all monitored temperature for the last two weeks.

From 9/22 noon to 9/27 noon and 9/30 to 10/2 noon apparently reasonable temperature regulation was achieved.

This period is shown enlarged in the two figures,

2006-9-23_0-0-0_to_2006-10-2-_23-58-7-Undulator17Temps.jpg

2006-9-23_0-0-0_to_2006-10-2-_23-58-7-Undulator102Temps.jpg ,

which show the temperatures in the indicated 10-day period for the

Undulators 17 on the Dover bench and 102 on the Kugler bench,

respectively

The temperatures shown are those of sensors at the

start(upstream)/middle/end(downstream) top half of undulator,

bottom half of undulator (in about the middle), as well as

(for undulator 17/Dover bench) on the granite of the bench.

Red shows tha air temperature near the undulator,

and yellow the air near the rack (sensor on post near south entrance).

A vertical bar on the bottom, e.g. ‘|---28’ marks the beginning of a calendar day ( the second ‘|’ marks noon on that day)

The following can be noticed:

- All Dover bench temperatures are 20.1 to 20.25 deg C,  that is 0.15 deg too warm.

- On 9/23 to 25 morning, and 10/1 to 2 morning, the system regulates quite well, to +/- 0.03 deg C.

- 9/28-29 there is a dip, perhaps following some repair.

- The peak on 9/30 ~14:58 is due to single (mis-)measurement preceding an outage until 16:47

(network disturbance? Problem accessing calibration files?)

- There are various temperature differences:

-  For Undulator 17, Start middle bottom seems to be warmer by 0.1 deg than end, air near

undulator(measured closer to end), and granite.

- All Kugler bench/Undulator 102 temperatures are about 0.1 deg colder  than Dover bench

temperatures.

To address the higher temperature of the Dover bench, Yuri had asked  for a lowering of the setpoint.

As shown in the temperature time history for the last 4 days below,

2006-10-1_0-0-0_to_2006-10-4_21-19-27-Undulator17Temps.jpg

2006-10-1_0-0-0_to_2006-10-4_21-19-27-Undulator102Temps.jpg

the temperature is still dropping.

These figures also shows good regulation on Oct1 to Oct2 ~noon.

II. Extraction of cooling times.

From the limited and noisy data it is difficult to extract a reliable estimate for the time required until an undulator is in equilibrium with the surrounding air.

The Figure 2006-9-28-drop17.jpg below shows the temperature drop seen on 9/28, when the air temperature near undulator 17 fell from ~20.13  to 20.08 deg C. (red curve; ignore 2 peaks at 11:30, 17:30, due to people standing close), beginning at ~8 a.m, and reaching a new  stationary value about 3 hours later.

The undulator 'end' temperature (green curve) began dropping ~ 1 1/2 hours later, and reached the same value as the air temperature at ~18:00, that is about 10 hours later.

Considering that the air temperature drop occured over 3 hours, one can estimate the time to equilibrium (on the surface, where  measured) to be more than 7, and less than 10 hours.

The other undulator temperatures also dropped, and came to equilibrium in about the same time. Their equilibrium is however about 0.1 degree  higher than that of the undulator 'end' temperature.

In Figure 2006-9-28-drop102.jpg below the contemperaneous temperature drop of undulator 102

on the Kugler bench is shown

III. Conclusion

It seems that the temperature regulation has been mostly achieved, however, the problem now

is  fine tuning, in particular the differences in temperature between different parts of the MMF

(such as Kugler vs Dover bench, and upstream/downstream end of undulator).