# Y Strainer Mesh Measurements

Scott Anderson 6/9/2026

Measurements were made on 3 sizes of mesh filters for the type of Y strainer which are installed in various part of the accelerator to try to prevent clogging of the beam line components. Tests were performed on a 2Q10 and two 1.0D22.625 Dipoles hooked up in parallel.  The 2Q10 has a nominal flow of ~0.64 gpm and the two 1.0D22.625 Dipoles  in parallel have a total flow of ~2.2 gpm.  The Tests were done at ~ delta pressure of 117-118 psi. Measurements were made using no filter, a 20 mess filter (0.84 mm diameter),  a 100 filter (0.149 mm diameter) and a 200 mesh filter (0.075 mm diameter)

The measurements show that none of the filters caused any loss in flow.   The data is on the magnetic measurements site at https:

//www-group.slac.stanford.edu/met/MagMeas/MAGDATA/LCLS-II/Water_System/Y_Strainer_Mesh/